## Sheet1
WADI Attackdata colleced
| New _attack _points | Start Date (Time) | End Date (Time)
| New _attack _points | 9-10-17 ( 6:00:00 PM) | 11-10-17 (6:00:00 PM)
S.No | Date | Start Time | End Time | Attack Point (s) | Initial State of the Attack Point(s) | State of The Attack point(s) | Impact | Remarks
1 | 2017-10-09 | 19:25 | 19:50 | 1MV001 | 1MV001-CLOSE | 1MV001-OPEN | Overflow of primary grid tank
2 | 2017-10-10 | 10:24 | 10:34 | 1FIT001 | No flow through 1FIT001 | False readings to 1FIT001 | Chemical dosing pumps start (increase of chemical dosing) | No increase in level in primary grid
3 | 2017-10-10 | 10:55 | 11:24 | 2LIT002 | Level at 70% | Increase the level from 70% to 80% fast rate and decrease the level from 80% to 70% slow rate | Drain the evevated reservoir tank | Stealthy attack
2 | 2017-10-10 | 11:08 | 11:12 | 1AIT001 | 176 | 640 | Raw water tank drain values opens (IMpact is obesrved till 11:27:16 AM)
5 | 1947-10-10 | 11.30:40 | 11:45 | 2MCV101, 2MCV201 | 22, 29,22,20,9,10 | All inlet valve positions brought to 0% position | No water to consumers
2MCV301,2MCV401
2MCV501, 2MCV601
6 | 2017-10-10 | 13:40 | 13:51 | 2MCV101, 2MCv201 | In Close postion | Open these valves to 50%
Attack sequene as follows: send contaminated water to Eelvated Reservoir tank by setting 1AIT002 to 6 and open 2MV003
7 | 2017-10-10 | 14:48 | 15:00 | 1_AIT_002 | Value at 0.5 | Set value to 6 | Drain valves-1MV002 and 1MV002 Open
| 2017-10-10 | 14:54 | 15:01 | 2MV003 | Close | Open | Supply contaminated water to ER tank
8 | 2017-10-10 | 17:40 | 17:50 | 2MCV007 | Close | Open to 30% | Water leakage
9 | 2017-10-11 | 10:55 | 10:56 | 1-P-005 On and 1-P-006 OFF | OFF | ON | Pipe bursts
Attack sequence as follows: Randomized attack
1. Wait till 2LIT002 reaches to 70%
2. Bring 1LIT001 to 40%
3. Launch attack on 1MV001 randomly. When water level in primary tank goes above 40 turn off the valve
10 | 2017-10-11 | 11:18 | 11:31 | 1MV001 | Close-Open | Open-Close | Damage 1MV001 and raw water pump and after some time ER tank drains
11 | 2017-07-11 | 11:37 | 11:47 | 2MCV007 | Close | Set at 50% | Booster will never turn on as 2FIT002 shows the reading > Total consumpyion flow rate
12 | 2017-07-11 | 11:59 | 12:05 | 2MCV007 | close | Set at 100% by gradually increasing 10% | In this case booster is On but 2MCV007 is open to waste the water
13 | 2017-07-11 | 12:08 | 12:11 | 2PIC003 | Set point is at 1 Bar | Set point to 0.25 bar | Intermittent supply to consumer tanks
14 | 2017-07-11 | 12:16 | 12:26 | 1P001and 1P003 | ON | OFF | Stop chmical dosing to the raw water tank
15 | 2017-07-11 | 15:26 | 15:37 | 2LIT002 | At 70% | Increase the level from 70% to 80% slow rate and decrease the level from 80% to 70% fast rate | Overflow of Elevated Reservoir tank | Stealthy attack